## Demands
ifc_guid | room_name | media_type | hvac_system_type | kind | value | unit
1e7aiH8Sn8fgWT34gsecs0 | Lagerraum | HEI | HEI | LOAD | 300 | W
1e7aiH8Sn8fgWT34gsecs0 | Lagerraum | LUE | LUE | FLOW | 15 | m3/h
1AjrabScTD7QDGtcwTOelF | Lagerraum | HEI | HEI | LOAD | 750 | W
1AjrabScTD7QDGtcwTOelF | Lagerraum | LUE | LUE | FLOW | 40 | m3/h
38ZWYAAYT3vu3w7nEOjRX9 | Hauswart | HEI | HEI | LOAD | 1550 | W
38ZWYAAYT3vu3w7nEOjRX9 | Hauswart | LUE | LUE | FLOW | 100 | m3/h
38ZWYAAYT3vu3w7nEOjRX9 | Hauswart | SAN | SAN | FLOW | 0.05 | l/s
0WXx9SLDn4veY22LFyMZpR | Lagerraum | HEI | HEI | LOAD | 750 | W
0WXx9SLDn4veY22LFyMZpR | Lagerraum | LUE | LUE | FLOW | 40 | m3/h
2fq$TLEG196gRjylkOPPt1 | Lagerraum | HEI | HEI | LOAD | 750 | W
2fq$TLEG196gRjylkOPPt1 | Lagerraum | LUE | LUE | FLOW | 40 | m3/h
2Fd3QJrEL8KeGvReeX8pzg | WC Bad Dusche | HEI | HEI | LOAD | 400 | W
2Fd3QJrEL8KeGvReeX8pzg | WC Bad Dusche | LUE | LUE | FLOW | 90 | m3/h
2Fd3QJrEL8KeGvReeX8pzg | WC Bad Dusche | SAN | SAN | FLOW | 0.2 | l/s
2h1BgBjgT1de_eNsTp1uud | Sitzungszimmer | HEI | HEI | LOAD | 3600 | W
2h1BgBjgT1de_eNsTp1uud | Sitzungszimmer | LUE | LUE | FLOW | 680 | m3/h
3SAD0c$KzCjwNFJKsTbYlX | Küche / Pausenraum | HEI | HEI | LOAD | 3450 | W
3SAD0c$KzCjwNFJKsTbYlX | Küche / Pausenraum | LUE | LUE | FLOW | 375 | m3/h
3SAD0c$KzCjwNFJKsTbYlX | Küche / Pausenraum | SAN | SAN | FLOW | 0.12 | l/s
07Q$ZAhHr9G9v1aKAjwyOA | Laborraum | HEI | HEI | LOAD | 2850 | W
07Q$ZAhHr9G9v1aKAjwyOA | Laborraum | LUE | LUE | FLOW | 265 | m3/h
07Q$ZAhHr9G9v1aKAjwyOA | Laborraum | SAN | SAN | FLOW | 0.05 | l/s
2pGZzOqrP3QgX198DnmsPP | Grossraumbüro | HEI | HEI | LOAD | 4150 | W
2pGZzOqrP3QgX198DnmsPP | Grossraumbüro | LUE | LUE | FLOW | 395 | m3/h
015OTJ3jz9LfvJSOtjdwqK | Einzelbüro | HEI | HEI | LOAD | 1750 | W
015OTJ3jz9LfvJSOtjdwqK | Einzelbüro | LUE | LUE | FLOW | 125 | m3/h
0qsyONUOnA7uV4ziubso__ | Grossraumbüro | HEI | HEI | LOAD | 4850 | W
0qsyONUOnA7uV4ziubso__ | Grossraumbüro | LUE | LUE | FLOW | 470 | m3/h
2SamNHDVH87BoWSt7usIhV | Einzelbüro | HEI | HEI | LOAD | 2200 | W
2SamNHDVH87BoWSt7usIhV | Einzelbüro | LUE | LUE | FLOW | 155 | m3/h
2RQfxNTAL9q9ncgRSekcCr | Grossraumbüro | HEI | HEI | LOAD | 2900 | W
2RQfxNTAL9q9ncgRSekcCr | Grossraumbüro | LUE | LUE | FLOW | 290 | m3/h
0pgni$2or6XO_NrWyexSdA | Sitzungszimmer | HEI | HEI | LOAD | 3600 | W
0pgni$2or6XO_NrWyexSdA | Sitzungszimmer | LUE | LUE | FLOW | 680 | m3/h
3zFj_sKlT5DxU$pSRK_gVt | Sitzungszimmer | HEI | HEI | LOAD | 1550 | W
3zFj_sKlT5DxU$pSRK_gVt | Sitzungszimmer | LUE | LUE | FLOW | 320 | m3/h
3mL9nzYdLAm9c0EQUdM5fJ | Gruppenbüro | HEI | HEI | LOAD | 3800 | W
3mL9nzYdLAm9c0EQUdM5fJ | Gruppenbüro | LUE | LUE | FLOW | 270 | m3/h
2pJJabSVnA7vCOzjrF1EXy | Gruppenbüro | HEI | HEI | LOAD | 3800 | W
2pJJabSVnA7vCOzjrF1EXy | Gruppenbüro | LUE | LUE | FLOW | 270 | m3/h
25DKmW5BbDpRgm_r8VP1E4 | Einzelbüro | HEI | HEI | LOAD | 1700 | W
25DKmW5BbDpRgm_r8VP1E4 | Einzelbüro | LUE | LUE | FLOW | 120 | m3/h
2ahuO8g9nAWgXNPfOxqAcH | Gruppenbüro | HEI | HEI | LOAD | 3800 | W
2ahuO8g9nAWgXNPfOxqAcH | Gruppenbüro | LUE | LUE | FLOW | 270 | m3/h
0FEj4ooyP1p9fzLNWGJrxo | Grossraumbüro | HEI | HEI | LOAD | 5000 | W
0FEj4ooyP1p9fzLNWGJrxo | Grossraumbüro | LUE | LUE | FLOW | 470 | m3/h
3wbDXDzzf0jOcow3chbfaR | Gruppenbüro | HEI | HEI | LOAD | 3800 | W
3wbDXDzzf0jOcow3chbfaR | Gruppenbüro | LUE | LUE | FLOW | 270 | m3/h
0NpEzY8OT02On0zCVFS5Hs | Sitzungszimmer | HEI | HEI | LOAD | 1500 | W
0NpEzY8OT02On0zCVFS5Hs | Sitzungszimmer | LUE | LUE | FLOW | 280 | m3/h
0LlUX5r1X3JPY8XXWFiCYt | Garderobe | HEI | HEI | LOAD | 600 | W
0LlUX5r1X3JPY8XXWFiCYt | Garderobe | LUE | LUE | FLOW | 85 | m3/h
0LlUX5r1X3JPY8XXWFiCYt | Garderobe | SAN | SAN | FLOW | 0.1 | l/s
1FLmg2I$XAnguWrSBdjIRl | WC Bad Dusche | HEI | HEI | LOAD | 400 | W
1FLmg2I$XAnguWrSBdjIRl | WC Bad Dusche | LUE | LUE | FLOW | 90 | m3/h
1FLmg2I$XAnguWrSBdjIRl | WC Bad Dusche | SAN | SAN | FLOW | 0.2 | l/s
1kOe4UIsf3bfsztm3YCt3f | Sitzungszimmer | HEI | HEI | LOAD | 3600 | W
1kOe4UIsf3bfsztm3YCt3f | Sitzungszimmer | LUE | LUE | FLOW | 680 | m3/h
3lnh0HVqz9We$buYKUZl5a | Küche / Pausenraum | HEI | HEI | LOAD | 3450 | W
3lnh0HVqz9We$buYKUZl5a | Küche / Pausenraum | LUE | LUE | FLOW | 375 | m3/h
3lnh0HVqz9We$buYKUZl5a | Küche / Pausenraum | SAN | SAN | FLOW | 0.12 | l/s
2cvFHPSVv2GOruxW2tCMZc | Laborraum | HEI | HEI | LOAD | 2850 | W
2cvFHPSVv2GOruxW2tCMZc | Laborraum | LUE | LUE | FLOW | 265 | m3/h
2cvFHPSVv2GOruxW2tCMZc | Laborraum | SAN | SAN | FLOW | 0.05 | l/s
1qCFa03a50Ieu_zRRtK_6c | Grossraumbüro | HEI | HEI | LOAD | 4150 | W
1qCFa03a50Ieu_zRRtK_6c | Grossraumbüro | LUE | LUE | FLOW | 395 | m3/h
0Edx_lA7n27xL1O3fBRKdi | Einzelbüro | HEI | HEI | LOAD | 1750 | W
0Edx_lA7n27xL1O3fBRKdi | Einzelbüro | LUE | LUE | FLOW | 125 | m3/h
0uJDDHaqj2OBEjYZWIR20V | Grossraumbüro | HEI | HEI | LOAD | 4850 | W
0uJDDHaqj2OBEjYZWIR20V | Grossraumbüro | LUE | LUE | FLOW | 470 | m3/h
1aInDLaLTEGO8FhAnE7Aws | Einzelbüro | HEI | HEI | LOAD | 2200 | W
1aInDLaLTEGO8FhAnE7Aws | Einzelbüro | LUE | LUE | FLOW | 155 | m3/h
2sO2Ja0Fn1sPvabENsgKZD | Grossraumbüro | HEI | HEI | LOAD | 2900 | W
2sO2Ja0Fn1sPvabENsgKZD | Grossraumbüro | LUE | LUE | FLOW | 290 | m3/h
126zlhQzH7oOuwMK1pw89I | Sitzungszimmer | HEI | HEI | LOAD | 3600 | W
126zlhQzH7oOuwMK1pw89I | Sitzungszimmer | LUE | LUE | FLOW | 680 | m3/h
17Io2Hts95I9gHEWzgvDeg | Sitzungszimmer | HEI | HEI | LOAD | 1550 | W
17Io2Hts95I9gHEWzgvDeg | Sitzungszimmer | LUE | LUE | FLOW | 320 | m3/h
1hr6l4g7DDbOgIq0bX27Xn | Gruppenbüro | HEI | HEI | LOAD | 3800 | W
1hr6l4g7DDbOgIq0bX27Xn | Gruppenbüro | LUE | LUE | FLOW | 270 | m3/h
1Z2_5Q$ovC5xywCbSXXBf5 | Gruppenbüro | HEI | HEI | LOAD | 3800 | W
1Z2_5Q$ovC5xywCbSXXBf5 | Gruppenbüro | LUE | LUE | FLOW | 270 | m3/h
1WIC1mey9EKQTZ_pjd_cXN | Einzelbüro | HEI | HEI | LOAD | 1700 | W
1WIC1mey9EKQTZ_pjd_cXN | Einzelbüro | LUE | LUE | FLOW | 120 | m3/h
1vDsO_9E579gQeaTViU$sn | Gruppenbüro | HEI | HEI | LOAD | 3800 | W
1vDsO_9E579gQeaTViU$sn | Gruppenbüro | LUE | LUE | FLOW | 270 | m3/h
19ALEAFkP6Yvncl0c8d7fl | Grossraumbüro | HEI | HEI | LOAD | 5000 | W
19ALEAFkP6Yvncl0c8d7fl | Grossraumbüro | LUE | LUE | FLOW | 470 | m3/h
1_Ydnth454jRS6rWTfK_ew | Gruppenbüro | HEI | HEI | LOAD | 3800 | W
1_Ydnth454jRS6rWTfK_ew | Gruppenbüro | LUE | LUE | FLOW | 270 | m3/h
0ekbaY4JD1gBRg3osTm9LZ | Sitzungszimmer | HEI | HEI | LOAD | 1500 | W
0ekbaY4JD1gBRg3osTm9LZ | Sitzungszimmer | LUE | LUE | FLOW | 280 | m3/h
02jOKnhlr4288_RpavstYK | Garderobe | HEI | HEI | LOAD | 600 | W
02jOKnhlr4288_RpavstYK | Garderobe | LUE | LUE | FLOW | 85 | m3/h
02jOKnhlr4288_RpavstYK | Garderobe | SAN | SAN | FLOW | 0.1 | l/s
2H0QiOBf52rgW7Qtn44C6V | WC Bad Dusche | HEI | HEI | LOAD | 400 | W
2H0QiOBf52rgW7Qtn44C6V | WC Bad Dusche | LUE | LUE | FLOW | 90 | m3/h
2H0QiOBf52rgW7Qtn44C6V | WC Bad Dusche | SAN | SAN | FLOW | 0.2 | l/s
1jZ5QUYN95QBjToVg_DPGY | Sitzungszimmer | HEI | HEI | LOAD | 3600 | W
1jZ5QUYN95QBjToVg_DPGY | Sitzungszimmer | LUE | LUE | FLOW | 680 | m3/h
2PeGESusj8Th0NXnlF1Ukl | Küche / Pausenraum | HEI | HEI | LOAD | 3450 | W
2PeGESusj8Th0NXnlF1Ukl | Küche / Pausenraum | LUE | LUE | FLOW | 375 | m3/h
2PeGESusj8Th0NXnlF1Ukl | Küche / Pausenraum | SAN | SAN | FLOW | 0.12 | l/s
14GsnpEA50IuDhLnWpxh1X | Laborraum | HEI | HEI | LOAD | 2850 | W
14GsnpEA50IuDhLnWpxh1X | Laborraum | LUE | LUE | FLOW | 265 | m3/h
14GsnpEA50IuDhLnWpxh1X | Laborraum | SAN | SAN | FLOW | 0.05 | l/s
1uhntHvVHFP8Vt1mwfuPTC | Grossraumbüro | HEI | HEI | LOAD | 4150 | W
1uhntHvVHFP8Vt1mwfuPTC | Grossraumbüro | LUE | LUE | FLOW | 395 | m3/h
1oWAI1Q9v7wuhHbBOyjZGi | Einzelbüro | HEI | HEI | LOAD | 1750 | W
1oWAI1Q9v7wuhHbBOyjZGi | Einzelbüro | LUE | LUE | FLOW | 125 | m3/h
2alSUWKlnEthoswo$PRPkY | Grossraumbüro | HEI | HEI | LOAD | 4850 | W
2alSUWKlnEthoswo$PRPkY | Grossraumbüro | LUE | LUE | FLOW | 470 | m3/h
3yN9_Xv1XFGuydBbvrKb2I | Einzelbüro | HEI | HEI | LOAD | 2200 | W
3yN9_Xv1XFGuydBbvrKb2I | Einzelbüro | LUE | LUE | FLOW | 155 | m3/h
12DwbiVxj8VuJtf4$JBDRn | Grossraumbüro | HEI | HEI | LOAD | 2900 | W
12DwbiVxj8VuJtf4$JBDRn | Grossraumbüro | LUE | LUE | FLOW | 290 | m3/h
3Hr71sZj9BVQKrp0Y4vHw_ | Sitzungszimmer | HEI | HEI | LOAD | 3600 | W
3Hr71sZj9BVQKrp0Y4vHw_ | Sitzungszimmer | LUE | LUE | FLOW | 680 | m3/h
2ZcOAyGNj7x9Xm78qHCjOh | Sitzungszimmer | HEI | HEI | LOAD | 1550 | W
2ZcOAyGNj7x9Xm78qHCjOh | Sitzungszimmer | LUE | LUE | FLOW | 320 | m3/h
1jNl__dP16hACFn5J7kor7 | Gruppenbüro | HEI | HEI | LOAD | 3800 | W
1jNl__dP16hACFn5J7kor7 | Gruppenbüro | LUE | LUE | FLOW | 270 | m3/h
1bChNTqYT7DfOrORFtqCpx | Gruppenbüro | HEI | HEI | LOAD | 3800 | W
1bChNTqYT7DfOrORFtqCpx | Gruppenbüro | LUE | LUE | FLOW | 270 | m3/h
2lztAC9Fb3Bu462O_Gbyqi | Einzelbüro | HEI | HEI | LOAD | 1700 | W
2lztAC9Fb3Bu462O_Gbyqi | Einzelbüro | LUE | LUE | FLOW | 120 | m3/h
0S4m5D_7T4_g7jzLOhIOQp | Gruppenbüro | HEI | HEI | LOAD | 3800 | W
0S4m5D_7T4_g7jzLOhIOQp | Gruppenbüro | LUE | LUE | FLOW | 270 | m3/h
3ZqhFyHEzFnxIZyj_YZija | Grossraumbüro | HEI | HEI | LOAD | 5000 | W
3ZqhFyHEzFnxIZyj_YZija | Grossraumbüro | LUE | LUE | FLOW | 470 | m3/h
2z0pEBVX97teZeQ8DPf7s1 | Gruppenbüro | HEI | HEI | LOAD | 3800 | W
2z0pEBVX97teZeQ8DPf7s1 | Gruppenbüro | LUE | LUE | FLOW | 270 | m3/h
0PtzbuTuD67QX3dFqpVR3G | Sitzungszimmer | HEI | HEI | LOAD | 1500 | W
0PtzbuTuD67QX3dFqpVR3G | Sitzungszimmer | LUE | LUE | FLOW | 280 | m3/h
3AP3M9CFD8TPvhiv$v0MoY | Garderobe | HEI | HEI | LOAD | 600 | W
3AP3M9CFD8TPvhiv$v0MoY | Garderobe | LUE | LUE | FLOW | 85 | m3/h
3AP3M9CFD8TPvhiv$v0MoY | Garderobe | SAN | SAN | FLOW | 0.1 | l/s
1mNjB9RH5Dcw0xuDRfC9KF | WC Bad Dusche | HEI | HEI | LOAD | 400 | W
1mNjB9RH5Dcw0xuDRfC9KF | WC Bad Dusche | LUE | LUE | FLOW | 90 | m3/h
1mNjB9RH5Dcw0xuDRfC9KF | WC Bad Dusche | SAN | SAN | FLOW | 0.2 | l/s

## Rooms
ifc_guid | storey | room_code | room_name | area_m2 | height_m | heated_status | occupancy | category | heat_w_m2 | air_m3h_m2 | air_m3h_person | air_min_m3h | water_default_ls | water_override_ls | HEI_W | LUE_m3h | SAN_l/s | note
1e7aiH8Sn8fgWT34gsecs0 | UG | 11 | Lagerraum | 28.35 | 2.05 | kalt | 0 | STORAGE | 20 | 0.5 | 0 | 10 | 0 |  | 300 | 15 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Lagerhalle.
1AjrabScTD7QDGtcwTOelF | UG | 12 | Lagerraum | 76.44 | 2.05 | kalt | 0 | STORAGE | 20 | 0.5 | 0 | 10 | 0 |  | 750 | 40 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Lagerhalle.
3hpHpkcUj9Vwf8TX00VY7$ | UG | 13 | Technikzentrale | 97.94 | 2.05 | unbeheizt | 0 | TECHNICAL | 10 | 1.5 | 0 | 20 | 0 |  | 0 | 145 | 0 | Estimated from IFC room name, occupancy type and area.
38ZWYAAYT3vu3w7nEOjRX9 | UG | 14 | Hauswart | 34.08 | 2.05 | beheizt | 2 | HOUSEKEEPING | 45 | 3 | 20 | 40 | 0.05 |  | 1550 | 100 | 0.05 | Estimated from IFC room name, occupancy type and area.
0WXx9SLDn4veY22LFyMZpR | UG | 15 | Lagerraum | 76.44 | 2.05 | kalt | 0 | STORAGE | 20 | 0.5 | 0 | 10 | 0 |  | 750 | 40 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Lagerhalle.
0X4Q7Ahhn9oBN510bvdGJ7 | UG | 16 | Technikzentrale | 99.84 | 2.05 | unbeheizt | 0 | TECHNICAL | 10 | 1.5 | 0 | 20 | 0 |  | 0 | 150 | 0 | Estimated from IFC room name, occupancy type and area.
2fq$TLEG196gRjylkOPPt1 | UG | 17 | Lagerraum | 76.44 | 2.05 | kalt | 0 | STORAGE | 20 | 0.5 | 0 | 10 | 0 |  | 750 | 40 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Lagerhalle.
0r0GK22SP4VvC6JLL1U4uW | UG | 23 | Lift | 21.6 | 2.05 | unbeheizt | 0 | LIFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
1n99Mc5s10ERHmxOHpNOCU | UG | 24 | Treppenhaus | 157.44 | 2.05 | kalt | 0 | STAIR | 15 | 1 | 0 | 15 | 0 |  | 1550 | 155 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Treppenhaus.
3FOeTu6pnBkexhLeeY6q63 | UG | 25 | Korridor | 99.84 | 2.05 | beheizt | 0 | CORRIDOR | 25 | 1.5 | 0 | 20 | 0 |  | 2500 | 150 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Verkehrsfläche.
1po6wfw1L6Du_SCcMQzf0s | UG | 26 | Korridor | 11.04 | 2.05 | beheizt | 0 | CORRIDOR | 25 | 1.5 | 0 | 20 | 0 |  | 300 | 20 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Verkehrsfläche.
2Fd3QJrEL8KeGvReeX8pzg | UG | 32 | WC Bad Dusche | 11.04 | 2.05 | beheizt | 0 | SANITARY | 35 | 8 | 0 | 60 | 0.2 |  | 400 | 90 | 0.2 | Estimated from IFC room name, occupancy type and area. OccupancyType: WC, Bad, Dusche.
0x1Y5hR8vA9ercNZvS03ni | UG | 41 | Schacht | 5.85 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
39i2X4imzA3xbaLDv4VrWC | UG | 42 | Schacht | 13.44 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
2Nsyr2vxz8zf9cCjzDG6Ws | UG | 43 | Schacht | 1.44 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
1hgAbhFVn97RAYzOOVFZvj | UG | 44 | Schacht | 2.4 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
1SloLv2tj0dv9VJESW7q62 | UG | 45 | Schacht | 6.24 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
2h1BgBjgT1de_eNsTp1uud | EG | 01 | Sitzungszimmer | 65.25 | 2.05 | beheizt | 17 | MEETING | 55 | 4.5 | 40 | 60 | 0 |  | 3600 | 680 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Sitzungszimmer.
3SAD0c$KzCjwNFJKsTbYlX | EG | 02 | Küche / Pausenraum | 57.6 | 2.05 | beheizt | 6 | KITCHEN_BREAK | 60 | 6.5 | 20 | 150 | 0.12 |  | 3450 | 375 | 0.12 | Estimated from IFC room name, occupancy type and area. OccupancyType: Küche, Teeküche.
07Q$ZAhHr9G9v1aKAjwyOA | EG | 03 | Laborraum | 44.1 | 2.05 | beheizt | 4 | LAB | 65 | 6 | 50 | 120 | 0.05 |  | 2850 | 265 | 0.05 | Estimated from IFC room name, occupancy type and area. OccupancyType: Laborraum.
2pGZzOqrP3QgX198DnmsPP | EG | 04 | Grossraumbüro | 83.25 | 2.05 | beheizt | 11 | OPEN_OFFICE | 50 | 4 | 36 | 60 | 0 |  | 4150 | 395 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Grossraumbüro.
015OTJ3jz9LfvJSOtjdwqK | EG | 05 | Einzelbüro | 35.1 | 2.05 | beheizt | 2 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 1750 | 125 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
0qsyONUOnA7uV4ziubso__ | EG | 06 | Grossraumbüro | 96.75 | 2.05 | beheizt | 13 | OPEN_OFFICE | 50 | 4 | 36 | 60 | 0 |  | 4850 | 470 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Grossraumbüro.
2SamNHDVH87BoWSt7usIhV | EG | 07 | Einzelbüro | 44.1 | 2.05 | beheizt | 3 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 2200 | 155 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
2RQfxNTAL9q9ncgRSekcCr | EG | 08 | Grossraumbüro | 57.6 | 2.05 | beheizt | 8 | OPEN_OFFICE | 50 | 4 | 36 | 60 | 0 |  | 2900 | 290 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Grossraumbüro.
0pgni$2or6XO_NrWyexSdA | EG | 09 | Sitzungszimmer | 65.25 | 2.05 | beheizt | 17 | MEETING | 55 | 4.5 | 40 | 60 | 0 |  | 3600 | 680 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Sitzungszimmer.
3zFj_sKlT5DxU$pSRK_gVt | EG | 11 | Sitzungszimmer | 28.35 | 2.05 | beheizt | 8 | MEETING | 55 | 4.5 | 40 | 60 | 0 |  | 1550 | 320 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Sitzungszimmer.
3mL9nzYdLAm9c0EQUdM5fJ | EG | 12 | Gruppenbüro | 76.44 | 2.05 | beheizt | 7 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 3800 | 270 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
2pJJabSVnA7vCOzjrF1EXy | EG | 13 | Gruppenbüro | 76.44 | 2.05 | beheizt | 7 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 3800 | 270 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
25DKmW5BbDpRgm_r8VP1E4 | EG | 14 | Einzelbüro | 34.08 | 2.05 | beheizt | 2 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 1700 | 120 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
2ahuO8g9nAWgXNPfOxqAcH | EG | 15 | Gruppenbüro | 76.44 | 2.05 | beheizt | 7 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 3800 | 270 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
0FEj4ooyP1p9fzLNWGJrxo | EG | 16 | Grossraumbüro | 99.84 | 2.05 | beheizt | 13 | OPEN_OFFICE | 50 | 4 | 36 | 60 | 0 |  | 5000 | 470 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Grossraumbüro.
3wbDXDzzf0jOcow3chbfaR | EG | 17 | Gruppenbüro | 76.44 | 2.05 | beheizt | 7 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 3800 | 270 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
0NpEzY8OT02On0zCVFS5Hs | EG | 18 | Sitzungszimmer | 27.3 | 2.05 | beheizt | 7 | MEETING | 55 | 4.5 | 40 | 60 | 0 |  | 1500 | 280 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Sitzungszimmer.
0v3kwr_3TC0f6BpW6X61ei | EG | 21 | Korridor | 121.5 | 2.05 | beheizt | 0 | CORRIDOR | 25 | 1.5 | 0 | 20 | 0 |  | 3050 | 180 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Verkehrsfläche.
27ZZwzcOL3rBNGaX_lwWkQ | EG | 22 | Korridor | 76.5 | 2.05 | beheizt | 0 | CORRIDOR | 25 | 1.5 | 0 | 20 | 0 |  | 1900 | 115 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Verkehrsfläche.
0PDZBnJOr138By27RqElf6 | EG | 23 | Lift | 21.6 | 2.05 | unbeheizt | 0 | LIFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
3EKZ2O$tT8ew41UHY$Lfy5 | EG | 24 | Treppenhaus | 157.44 | 2.05 | kalt | 0 | STAIR | 15 | 1 | 0 | 15 | 0 |  | 1550 | 155 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Treppenhaus.
2khyYqZRr5Q81h5e2MHDAh | EG | 25 | Korridor | 99.84 | 2.05 | beheizt | 0 | CORRIDOR | 25 | 1.5 | 0 | 20 | 0 |  | 2500 | 150 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Verkehrsfläche.
35vqBCQobETByOjDARpKwG | EG | 26 | Korridor | 11.04 | 2.05 | beheizt | 0 | CORRIDOR | 25 | 1.5 | 0 | 20 | 0 |  | 300 | 20 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Verkehrsfläche.
0LlUX5r1X3JPY8XXWFiCYt | EG | 31 | Garderobe | 20.64 | 2.05 | beheizt | 0 | WARDROBE | 30 | 4 | 0 | 40 | 0.1 |  | 600 | 85 | 0.1 | Estimated from IFC room name, occupancy type and area. OccupancyType: Garderobe, Dusche.
1FLmg2I$XAnguWrSBdjIRl | EG | 32 | WC Bad Dusche | 11.04 | 2.05 | beheizt | 0 | SANITARY | 35 | 8 | 0 | 60 | 0.2 |  | 400 | 90 | 0.2 | Estimated from IFC room name, occupancy type and area. OccupancyType: WC, Bad, Dusche.
0lFBqgYZj8xe4O9FTGEoH1 | EG | 41 | Schacht | 5.85 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
2Wm8O7oJ9E0Rnyb5N8e_CR | EG | 42 | Schacht | 13.44 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
0P1jTQu5D8jeRBSvOj9hMQ | EG | 43 | Schacht | 1.44 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
1TyNWYz9f1A900VPKes2eJ | EG | 44 | Schacht | 2.4 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
10o3TPcOL7MPAmnFkeLkCc | EG | 45 | Schacht | 6.24 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
1kOe4UIsf3bfsztm3YCt3f | 1.OG | 01 | Sitzungszimmer | 65.25 | 2.05 | beheizt | 17 | MEETING | 55 | 4.5 | 40 | 60 | 0 |  | 3600 | 680 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Sitzungszimmer.
3lnh0HVqz9We$buYKUZl5a | 1.OG | 02 | Küche / Pausenraum | 57.6 | 2.05 | beheizt | 6 | KITCHEN_BREAK | 60 | 6.5 | 20 | 150 | 0.12 |  | 3450 | 375 | 0.12 | Estimated from IFC room name, occupancy type and area. OccupancyType: Küche, Teeküche.
2cvFHPSVv2GOruxW2tCMZc | 1.OG | 03 | Laborraum | 44.1 | 2.05 | beheizt | 4 | LAB | 65 | 6 | 50 | 120 | 0.05 |  | 2850 | 265 | 0.05 | Estimated from IFC room name, occupancy type and area. OccupancyType: Laborraum.
1qCFa03a50Ieu_zRRtK_6c | 1.OG | 04 | Grossraumbüro | 83.25 | 2.05 | beheizt | 11 | OPEN_OFFICE | 50 | 4 | 36 | 60 | 0 |  | 4150 | 395 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Grossraumbüro.
0Edx_lA7n27xL1O3fBRKdi | 1.OG | 05 | Einzelbüro | 35.1 | 2.05 | beheizt | 2 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 1750 | 125 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
0uJDDHaqj2OBEjYZWIR20V | 1.OG | 06 | Grossraumbüro | 96.75 | 2.05 | beheizt | 13 | OPEN_OFFICE | 50 | 4 | 36 | 60 | 0 |  | 4850 | 470 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Grossraumbüro.
1aInDLaLTEGO8FhAnE7Aws | 1.OG | 07 | Einzelbüro | 44.1 | 2.05 | beheizt | 3 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 2200 | 155 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
2sO2Ja0Fn1sPvabENsgKZD | 1.OG | 08 | Grossraumbüro | 57.6 | 2.05 | beheizt | 8 | OPEN_OFFICE | 50 | 4 | 36 | 60 | 0 |  | 2900 | 290 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Grossraumbüro.
126zlhQzH7oOuwMK1pw89I | 1.OG | 09 | Sitzungszimmer | 65.25 | 2.05 | beheizt | 17 | MEETING | 55 | 4.5 | 40 | 60 | 0 |  | 3600 | 680 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Sitzungszimmer.
17Io2Hts95I9gHEWzgvDeg | 1.OG | 11 | Sitzungszimmer | 28.35 | 2.05 | beheizt | 8 | MEETING | 55 | 4.5 | 40 | 60 | 0 |  | 1550 | 320 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Sitzungszimmer.
1hr6l4g7DDbOgIq0bX27Xn | 1.OG | 12 | Gruppenbüro | 76.44 | 2.05 | beheizt | 7 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 3800 | 270 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
1Z2_5Q$ovC5xywCbSXXBf5 | 1.OG | 13 | Gruppenbüro | 76.44 | 2.05 | beheizt | 7 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 3800 | 270 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
1WIC1mey9EKQTZ_pjd_cXN | 1.OG | 14 | Einzelbüro | 34.08 | 2.05 | beheizt | 2 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 1700 | 120 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
1vDsO_9E579gQeaTViU$sn | 1.OG | 15 | Gruppenbüro | 76.44 | 2.05 | beheizt | 7 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 3800 | 270 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
19ALEAFkP6Yvncl0c8d7fl | 1.OG | 16 | Grossraumbüro | 99.84 | 2.05 | beheizt | 13 | OPEN_OFFICE | 50 | 4 | 36 | 60 | 0 |  | 5000 | 470 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Grossraumbüro.
1_Ydnth454jRS6rWTfK_ew | 1.OG | 17 | Gruppenbüro | 76.44 | 2.05 | beheizt | 7 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 3800 | 270 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
0ekbaY4JD1gBRg3osTm9LZ | 1.OG | 18 | Sitzungszimmer | 27.3 | 2.05 | beheizt | 7 | MEETING | 55 | 4.5 | 40 | 60 | 0 |  | 1500 | 280 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Sitzungszimmer.
1arlitlbrALeVkhUjamAFV | 1.OG | 21 | Korridor | 121.5 | 2.05 | beheizt | 0 | CORRIDOR | 25 | 1.5 | 0 | 20 | 0 |  | 3050 | 180 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Verkehrsfläche.
1Sx_MppbP15euZJQXf9Hs1 | 1.OG | 22 | Korridor | 76.5 | 2.05 | beheizt | 0 | CORRIDOR | 25 | 1.5 | 0 | 20 | 0 |  | 1900 | 115 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Verkehrsfläche.
0$tZUkcwLFifRDTMNCuM6F | 1.OG | 23 | Lift | 21.6 | 2.05 | unbeheizt | 0 | LIFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
1SkCv6K7n2dfGYxRt3Uniu | 1.OG | 24 | Treppenhaus | 157.44 | 2.05 | kalt | 0 | STAIR | 15 | 1 | 0 | 15 | 0 |  | 1550 | 155 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Treppenhaus.
0t3N7JNqj17RYFoTLVFqED | 1.OG | 25 | Korridor | 99.84 | 2.05 | beheizt | 0 | CORRIDOR | 25 | 1.5 | 0 | 20 | 0 |  | 2500 | 150 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Verkehrsfläche.
3ji8dLIY5EzQQB6_noyDZn | 1.OG | 26 | Korridor | 11.04 | 2.05 | beheizt | 0 | CORRIDOR | 25 | 1.5 | 0 | 20 | 0 |  | 300 | 20 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Verkehrsfläche.
02jOKnhlr4288_RpavstYK | 1.OG | 31 | Garderobe | 20.64 | 2.05 | beheizt | 0 | WARDROBE | 30 | 4 | 0 | 40 | 0.1 |  | 600 | 85 | 0.1 | Estimated from IFC room name, occupancy type and area. OccupancyType: Garderobe, Dusche.
2H0QiOBf52rgW7Qtn44C6V | 1.OG | 32 | WC Bad Dusche | 11.04 | 2.05 | beheizt | 0 | SANITARY | 35 | 8 | 0 | 60 | 0.2 |  | 400 | 90 | 0.2 | Estimated from IFC room name, occupancy type and area. OccupancyType: WC, Bad, Dusche.
3QoxyPyiH8Iv8pfUqOd0WG | 1.OG | 41 | Schacht | 5.85 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
3fudELvoT2nR_Qlp$aQZ$H | 1.OG | 42 | Schacht | 13.44 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
0sxzqxp3P5BvpqanP9TXWK | 1.OG | 43 | Schacht | 1.44 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
2k95g6LUzAEwkiEZqW3DsT | 1.OG | 44 | Schacht | 2.4 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
3YTtRhn4vC6Bdx0VwzDtBN | 1.OG | 45 | Schacht | 6.24 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
1jZ5QUYN95QBjToVg_DPGY | 2.OG | 01 | Sitzungszimmer | 65.25 | 2.05 | beheizt | 17 | MEETING | 55 | 4.5 | 40 | 60 | 0 |  | 3600 | 680 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Sitzungszimmer.
2PeGESusj8Th0NXnlF1Ukl | 2.OG | 02 | Küche / Pausenraum | 57.6 | 2.05 | beheizt | 6 | KITCHEN_BREAK | 60 | 6.5 | 20 | 150 | 0.12 |  | 3450 | 375 | 0.12 | Estimated from IFC room name, occupancy type and area. OccupancyType: Küche, Teeküche.
14GsnpEA50IuDhLnWpxh1X | 2.OG | 03 | Laborraum | 44.1 | 2.05 | beheizt | 4 | LAB | 65 | 6 | 50 | 120 | 0.05 |  | 2850 | 265 | 0.05 | Estimated from IFC room name, occupancy type and area. OccupancyType: Laborraum.
1uhntHvVHFP8Vt1mwfuPTC | 2.OG | 04 | Grossraumbüro | 83.25 | 2.05 | beheizt | 11 | OPEN_OFFICE | 50 | 4 | 36 | 60 | 0 |  | 4150 | 395 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Grossraumbüro.
1oWAI1Q9v7wuhHbBOyjZGi | 2.OG | 05 | Einzelbüro | 35.1 | 2.05 | beheizt | 2 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 1750 | 125 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
2alSUWKlnEthoswo$PRPkY | 2.OG | 06 | Grossraumbüro | 96.75 | 2.05 | beheizt | 13 | OPEN_OFFICE | 50 | 4 | 36 | 60 | 0 |  | 4850 | 470 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Grossraumbüro.
3yN9_Xv1XFGuydBbvrKb2I | 2.OG | 07 | Einzelbüro | 44.1 | 2.05 | beheizt | 3 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 2200 | 155 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
12DwbiVxj8VuJtf4$JBDRn | 2.OG | 08 | Grossraumbüro | 57.6 | 2.05 | beheizt | 8 | OPEN_OFFICE | 50 | 4 | 36 | 60 | 0 |  | 2900 | 290 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Grossraumbüro.
3Hr71sZj9BVQKrp0Y4vHw_ | 2.OG | 09 | Sitzungszimmer | 65.25 | 2.05 | beheizt | 17 | MEETING | 55 | 4.5 | 40 | 60 | 0 |  | 3600 | 680 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Sitzungszimmer.
2ZcOAyGNj7x9Xm78qHCjOh | 2.OG | 11 | Sitzungszimmer | 28.35 | 2.05 | beheizt | 8 | MEETING | 55 | 4.5 | 40 | 60 | 0 |  | 1550 | 320 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Sitzungszimmer.
1jNl__dP16hACFn5J7kor7 | 2.OG | 12 | Gruppenbüro | 76.44 | 2.05 | beheizt | 7 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 3800 | 270 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
1bChNTqYT7DfOrORFtqCpx | 2.OG | 13 | Gruppenbüro | 76.44 | 2.05 | beheizt | 7 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 3800 | 270 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
2lztAC9Fb3Bu462O_Gbyqi | 2.OG | 14 | Einzelbüro | 34.08 | 2.05 | beheizt | 2 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 1700 | 120 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
0S4m5D_7T4_g7jzLOhIOQp | 2.OG | 15 | Gruppenbüro | 76.44 | 2.05 | beheizt | 7 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 3800 | 270 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
3ZqhFyHEzFnxIZyj_YZija | 2.OG | 16 | Grossraumbüro | 99.84 | 2.05 | beheizt | 13 | OPEN_OFFICE | 50 | 4 | 36 | 60 | 0 |  | 5000 | 470 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Grossraumbüro.
2z0pEBVX97teZeQ8DPf7s1 | 2.OG | 17 | Gruppenbüro | 76.44 | 2.05 | beheizt | 7 | OFFICE | 50 | 3.5 | 36 | 40 | 0 |  | 3800 | 270 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Einzel-, Gruppenbüro.
0PtzbuTuD67QX3dFqpVR3G | 2.OG | 18 | Sitzungszimmer | 27.3 | 2.05 | beheizt | 7 | MEETING | 55 | 4.5 | 40 | 60 | 0 |  | 1500 | 280 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Sitzungszimmer.
0kmyz7CZj6JwYIdbAwAHGj | 2.OG | 21 | Korridor | 121.5 | 2.05 | beheizt | 0 | CORRIDOR | 25 | 1.5 | 0 | 20 | 0 |  | 3050 | 180 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Verkehrsfläche.
0coVUDnrrERB6CK338mkjp | 2.OG | 22 | Korridor | 76.5 | 2.05 | beheizt | 0 | CORRIDOR | 25 | 1.5 | 0 | 20 | 0 |  | 1900 | 115 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Verkehrsfläche.
2rf3pnwtzEbeks3Oqv4LqG | 2.OG | 23 | Lift | 21.6 | 2.05 | unbeheizt | 0 | LIFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
34ekzyiGn238hbkxgpMV6v | 2.OG | 24 | Treppenhaus | 157.44 | 2.05 | kalt | 0 | STAIR | 15 | 1 | 0 | 15 | 0 |  | 1550 | 155 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Treppenhaus.
0mUxeMcSXBHOspqtEHmPM$ | 2.OG | 25 | Korridor | 99.84 | 2.05 | beheizt | 0 | CORRIDOR | 25 | 1.5 | 0 | 20 | 0 |  | 2500 | 150 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Verkehrsfläche.
1Rh8ASh_j0Kgn9RIoUyJHX | 2.OG | 26 | Korridor | 11.04 | 2.05 | beheizt | 0 | CORRIDOR | 25 | 1.5 | 0 | 20 | 0 |  | 300 | 20 | 0 | Estimated from IFC room name, occupancy type and area. OccupancyType: Verkehrsfläche.
3AP3M9CFD8TPvhiv$v0MoY | 2.OG | 31 | Garderobe | 20.64 | 2.05 | beheizt | 0 | WARDROBE | 30 | 4 | 0 | 40 | 0.1 |  | 600 | 85 | 0.1 | Estimated from IFC room name, occupancy type and area. OccupancyType: Garderobe, Dusche.
1mNjB9RH5Dcw0xuDRfC9KF | 2.OG | 32 | WC Bad Dusche | 11.04 | 2.05 | beheizt | 0 | SANITARY | 35 | 8 | 0 | 60 | 0.2 |  | 400 | 90 | 0.2 | Estimated from IFC room name, occupancy type and area. OccupancyType: WC, Bad, Dusche.
1CFE2H6m9F3h92kYSVuict | 2.OG | 41 | Schacht | 5.85 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
2TFUQfoSr5MA9gW$xKvBHh | 2.OG | 42 | Schacht | 13.44 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
0nCDl96EH1eBpf_UZquDfx | 2.OG | 43 | Schacht | 1.44 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
1LTGzgabbEF8UCIF4Jegx1 | 2.OG | 44 | Schacht | 2.4 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.
1f$1icVJ9F8gLfub5rtniV | 2.OG | 45 | Schacht | 6.24 | 2.05 | unbeheizt | 0 | SHAFT | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | Estimated from IFC room name, occupancy type and area.

## Assumptions
category | heat_w_m2 | air_m3h_m2 | air_m3h_person | air_min_m3h | water_default_ls | description
OFFICE | 50 | 3.5 | 36 | 40 | 0 | Enclosed offices and group offices
OPEN_OFFICE | 50 | 4 | 36 | 60 | 0 | Open-plan office space
MEETING | 55 | 4.5 | 40 | 60 | 0 | Meeting and seminar rooms
LAB | 65 | 6 | 50 | 120 | 0.05 | Laboratory / practical rooms
KITCHEN_BREAK | 60 | 6.5 | 20 | 150 | 0.12 | Kitchenette and break room
SANITARY | 35 | 8 | 0 | 60 | 0.2 | WC / shower / washroom
WARDROBE | 30 | 4 | 0 | 40 | 0.1 | Changing room / wardrobe
HOUSEKEEPING | 45 | 3 | 20 | 40 | 0.05 | Janitor / service room
CORRIDOR | 25 | 1.5 | 0 | 20 | 0 | Circulation corridor
STAIR | 15 | 1 | 0 | 15 | 0 | Stairwell
STORAGE | 20 | 0.5 | 0 | 10 | 0 | Storage rooms
TECHNICAL | 10 | 1.5 | 0 | 20 | 0 | Technical / plant rooms
SHAFT | 0 | 0 | 0 | 0 | 0 | Vertical shafts
LIFT | 0 | 0 | 0 | 0 | 0 | Lift / elevator core